## Slide 1
Xiaohui “Joe” Zhou, PhD, PE
Iowa Energy Center
2013 BOMA Iowa
Des Moines, IA
April 16, 2013
Saving Money Through Building Energy Efficiency:
The Opportunities

## Slide 2: Outline
Introduction to Iowa Energy Center
Why Building Energy Efficiency is Important
Strategies to Improve Building Energy Efficiency
Steps to follow:
  Know your building’s present energy performance
  Analyze opportunities through an energy audit
  Explore building energy improvement options
  Monitor results

## Slide 3: About the Iowa Energy Center
A public, non-profit organization
Was created by the Iowa General Assembly and signed into law in 1990
Has a mission to serve Iowans through reliable, objective tools, and information
Is administered through Iowa State University
Has a 13-member Advisory Council representing key constituencies and stakeholders (as described in the 1990 Energy Efficiency Act)

## Slide 4: Our Mission
Advance Iowa’s energy efficiency and renewable energy use through transformative research, education, and demonstration
  Strive to increase energy efficiency in all areas of Iowa’s energy use
  Serve as a model for state efforts on energy efficiency and renewable energy
  Conduct and sponsor research on energy efficiency and conservation, as well as alternative energy based on renewable resources
  Assist Iowans in assessing energy-related technologies
  Support educational and demonstration programs

## Slide 5: Key Program Areas
Energy Efficiency
  Building
  Industrial
  Agricultural
  Transportation
Renewable Energy
  Biorenewable
  Solar
  Wind
Grants and Funding
  IEC Sponsored Grants
  Alternate Energy Revolving Loan Program
  Scholarships
Outreach
  Learning Institute for training and education
  Communications and Marketing

## Slide 6: Why Building Energy Efficiency is Important
The Big Picture
Chart: U.S. Primary Energy Consumption
| Industrial | Transportation | Buildings
Primary Energy Use in the U.S. | 30.6 | 28.1 | 41.3
*Based on the 2010 Energy Data Book by the Department of Energy; 1 Quads = 1 000 000 000 000 000.
Transportation
28%

## Slide 7: Why Building Energy Efficiency is Important
Commercial Building Energy End-Use Type Splits
Chart: 
| Lighting | Space Heating | Space Cooling | Ventilation | Refrigeration | Water Heating | Electronics | Computers | Cooking | Other (5) | Adjust to SEDS (6)
Sales | 0.147 | 0.261 | 0.093 | 0.062 | 0.047 | 0.067 | 0.028 | 0.026 | 0.022 | 0.126 | 0.122
*Based on the 2010 Energy Data Book by the Department of Energy

## Slide 8: Strategies to Improve Building Energy Efficiency
How much energy can be saved by doing what?
  7%~28% by implementing no cost or low-cost energy efficient measures through changes in building operations and management (O&M)
  3.5%~15.2% by changing occupant behavior
  9.4%~25% by retrofitting lighting
  7.3%~22.9% by calibrating HVAC control devices, improve control sequences, and monitoring energy use
  3.5%~15.9% through replacing old HVAC equipment with new energy efficient units
*Based on BOMA International BEEP 2006 report

## Slide 9: Strategies to Improve Building Energy Efficiency
Opportunities for Existing Buildings
  Reduce Energy Demand: plug loads, peak demand
  Improve Building Energy Efficiency: operations & management; energy audit and retro-commissioning
  Use Renewable Energy Source: wind, solar
  Financial Incentives: tax credits, utility rebates
*Existing buildings account for approximately 70% ~ 85% of buildings that will exist in 2030.

## Slide 10: Steps to Take
Know Your Building's Energy Performance
Analyze Opportunities through an Energy Audit
Explore Building Energy Improvement Options
Monitor Results

## Slide 11: Steps to Take: Know Your Building's Energy Performance
Know Your Building's Energy Performance
  Calculate Energy Utilization Index (EUI)
    Unit energy use for buildings in BTU/sq. ft. - year
  Calculate Energy Cost Index (ECI)
    Unit cost of energy for buildings in $/sq. ft. - year
*BTU = British Thermal Unit; 1 BTU ~= 0.293 Watt-Hour

## Slide 12: Steps to Take: Know Your Building's Energy Performance
Gross Office Building Area: |  |  | 12500 | sq. ft. |  | 
MONTH | Electricity |  | Natural Gas |  | Total | 
 | Cost | Office Bldg | Energy | Cost | Energy | Cost
 | $ | Total KWH | Therms | $ | kBTU | $
January | 608.8979 | 12835.4 | 427 | 397.11 | 86507.2202 | 1006.007898
February | 533.8115 | 9923.2 | 91 | 90.47 | 42967.8816 | 624.281456
March | 389.1015 | 6779 | 101 | 91.43 | 33236.727 | 480.5315275
April | 299.5248 | 4955.8 | 50 | 45.5 | 21914.1454 | 345.0247663
May | 509.1813 | 5520 | 10 | 17.92 | 19839.76 | 527.1013084
June | 529.8775 | 5728.7 | 5 | 14.12 | 20052.0531 | 543.9974705
July | 575.858 | 6367.8 | 5 | 14.49 | 22233.3014 | 590.3479565
August | 496.5895 | 5614 | 5 | 14.26 | 19660.582 | 510.8494889
September | 226.5405 | 3734.8 | 4 | 13.38 | 13146.8724 | 239.9205187
October | 394.9498 | 6555.8 | 5 | 14.21 | 22874.9454 | 409.1598217
November | 516.2209 | 9379.5 | 64 | 61.3 | 38412.2335 | 577.5209352
December | 547.3023 | 10953.7 | 121 | 111.33 | 49484.9781 | 658.632338
Total |  |  |  |  | 390330.7001 | 6513.375486
Average |  |  |  |  | 31.23 | 0.52
* 1 KWH = 3.412 kBTU; 1 Therm = 100 kBTU |  |  |  |  | EUI (kBTU/s.q ft. - year) | ECI ($/sq. ft. - year)

## Slide 13: Steps to Take: Know Your Building's Energy Performance
What is Building Energy Benchmarking and Benefits?
  Building Energy Benchmarking
    How did your building compare with similar buildings?
    Compared to self, within a portfolio, or nationally?
    Does your building energy performance meet energy code?
  Benefits
    Respond to rising energy costs
    Enhance your company's image and attract satisfied tenants
    Improve the marketability of your property by differentiating it from others

## Slide 14: Steps to Take: Know Your Building's Energy Performance
U.S. Climate Zone Map

## Slide 15: Steps to Take: Know Your Building's Energy Performance
City | Chicago | Denver | Minneapolis
Climate Zone | 5A | 5B | 6A
Large Office | 43 | 36 | 46
Medium Office | 48 | 41 | 54
Small Office | 51 | 45 | 57
Warehouse | 24 | 23 | 29
Stand-alone Retail | 81 | 69 | 93
Strip Mall | 85 | 72 | 99
Primary School | 65 | 58 | 75
Secondary School | 76 | 64 | 89
Supermarket | 195 | 179 | 208
Quick Service Restaurant | 657 | 604 | 713
Full Service Restaurant | 527 | 481 | 570
Hospital | 148 | 130 | 153
Outpatient Facility | 271 | 271 | 280
Small Hotel | 80 | 74 | 87
Large Hotel | 138 | 131 | 150
Mid-Rise Apartment | 47 | 41 | 54
DOE Commercial Building Benchmarks –
New Construction
EUIs (kBtu/sq. ft-yr)
October 2009

## Slide 16: Steps to Take: Know Your Building's Energy Performance
  Benchmarking Systems 1: EPA’s Energy Star Portfolio Manager
    Based on national survey 2003 CBECS database by EIA (Energy Information Administration)
    Provides a comparison for 15 commercial building types
    Scaled in 1 – 100 relative to similar buildings nationwide (highest number is the most energy efficient building)
    Building rating above 75 may receive Energy Star label
    http://www.energystar.gov/index.cfm?c=evaluate_performance.bus_PortfolioManager

## Slide 17: Steps to Take: Know Your Building's Energy Performance
Chart: 
| IAMU
Series 1 | 93
Series 2 | 7
Energy Star Rating

## Slide 18: Steps to Take: Know Your Building's Energy Performance
  Benchmarking Systems 2: ASHRAE Building Energy Quotient
    Ratings for both design and operation
    Requires more detailed information than the monthly utility bill
    Provides more detailed opportunity analysis
    http://buildingenergyquotient.org/

## Slide 19: Steps to Take: Know Your Building's Energy Performance
  Benchmarking Systems 3: U.S. Department of Energy Commercial Building Asset Score
    Still being developed
    Scale 1 - 100 (higher number is better)
    Intended to help identify inefficient areas in building energy
    http://www1.eere.energy.gov/buildings/commercial/assetscore.html

## Slide 20: Steps to Take: Know Your Building's Energy Performance

## Slide 21: Steps to Take: Know Your Building's Energy Performance

## Slide 22: Steps to Take: Know Your Building's Energy Performance
  Benchmarking Systems 4: Iowa Public Building Benchmarking System
    Web-based platform
    Iowa public buildings (now 1200+ buildings)
    Benchmarking ratio: Benchmark energy use based on current energy code. 1.0 = energy code compliant building (lower number is better)
    Also includes Energy Star rating (if applicable) and peer rating
    Currently recruiting up to 800 new buildings
    http://www.iowaenergycenter.org/

## Slide 23: Steps to Take: Know Your Building's Energy Performance

## Slide 24: Steps to Take: Analyze Opportunities
Setting Goals
  10%, 20%, or 30% compared with historical EUI?
  LEED for existing buildings? (O&M certification requires a minimum of 69 on ENERGY STAR rating)
  Benchmarking ratio below 1.0?
Strong Management Support

## Slide 25: Steps to Take: Analyze Opportunities
Analyze How and Where Did Energy Go - Prioritize
  Sub-Metering
  Energy Audits
    Level 1: Walk-through
    Level 2: Energy survey and analysis
    Level 3: Detailed analysis and capital
    -intensive modifications
    Utility programs – no cost or low-cost for qualified customers

## Slide 26: Steps to Take: Building Energy Improvement Options
Improve Building Operations – No Cost or Low-Cost
    Reduce HVAC equipment's occupancy hours
    Reduce lighting hours, use day lighting, or use occupancy sensors
    Replace/repair/calibrate sensors
    Use a programmable thermostat
    Relocate/shield temperature sensors
    Use economizer
    Use duct static pressure reset
    Use supply air temperature reset

## Slide 27: Steps to Take: Building Energy Improvement Options
    Use demand-controlled ventilation (DCV)
    Chilled water supply temperature reset
    Optimize heating water supply
    Optimal start/stop
    Tune HVAC control – check the thermostat schedule!
    Check minimum damper position
    Automated fault detection and diagnostics
    Best janitorial practices

## Slide 28: Steps to Take: Building Energy Improvement Options
Using improved duct static pressure reset strategy, saved ~37% of fan energy
in 3 month’s field testing in this 40,528 sq. ft building; ~$3839 / year .
Example:
Iowa State University Hixson-Lied Student Success Center

## Slide 29: Steps to Take: Building Energy Improvement Options
Management Improvements – Low-Cost or No Cost
    Make energy management a priority
    Require systems manuals (operation and maintenance, etc.)
    Invest in training and education for operators and occupants – change occupant behavior
    Establish purchasing criteria: Energy Star-labeled appliance/equipment, CFL, LED, etc.
    Insist on performance tracking and reporting

## Slide 30: Steps to Take: Building Energy Improvement Options
Lighting Retrofit
  Use occupancy sensors
  Use day lighting, photo cells, and dimming controls
  Replace with new energy efficient lighting
    Compact Fluorescent (CFL)
    Light-emitting Diode (LED)
    Fluorescent T8 or T5
  Use external/internal shading devices
While a modern office can be lit using <1W/sq. ft., most still use about 1.5~2W/sq. ft.

## Slide 31: Steps to Take: Building Energy Improvement Options
Example: Cedar Rapids Hy-Vee Parking Lot LED Lighting Study
Replacing 1000w Metal Halide with 309w LED
*Report is available at www.iowaenergycenter.org

## Slide 32: Steps to Take: Building Energy Improvement Options
*Report is available at www.iowaenergycenter.org
Metal Halide
Metal Halide
LED
LED

## Slide 33: Steps to Take: Building Energy Improvement Options
Cedar Rapids Hy-Vee Parking Lot LED Lighting Study
Chart: Average Daily Lighting Power Consumption (kWh/day)
| Metal Halide | LED
Series 1 | 11.85 | 3.62
69% Reduction
*Report is available at www.iowaenergycenter.org

## Slide 34: Steps to Take: Building Energy Improvement Options
Plug Loads Control
  Check your building's phantom loads
  Apply power management software: put equipment in sleep mode
  Use energy misers: vending miser, cooler miser, snack miser, plug miser, etc.

## Slide 35: Steps to Take: Building Energy Improvement Options
Fix Building Envelope Problems
  Increase insulation making sure it is installed correctly (roof, wall, etc.)
  Find and fix air leaks
  Upgrade windows
    At a minimum, use double-pane windows
    High efficiency low-e window
    Electro-chromic and thermo-chromic windows
    Window-to-Wall ratio should be < 35%

## Slide 36: Steps to Take: Building Energy Improvement Options
Upgrade HVAC System and/or Replace Old HVAC Equipment
  Any RTUs, electric boilers, or control systems that are older than 10~15 years
  Chillers, pumps, fans, boilers, motors older than 15~20 years
  Pneumatic control system of any age
  Consider adding Energy Recovery Unit (ERU)

## Slide 37: Steps to Take: Building Energy Improvement Options
  Upgrade to high efficiency fans and motors controlled with variable frequency drives (VFD)
  Convert constant-air-volume (CAV) system to variable-air-volume (VAV) system
  Change central domestic hot water systems to point-of-use water heaters; install high efficiency water heaters
  Many other options depending on the project

## Slide 38: Steps to Take: Building Energy Improvement Options
  Making the business case
    Simple payback = project cost / annual change in cash flow
    Net present value (NPV) – accounts for the time value of money
    Internal rate of return (IRR)
    Life-cycle cost analysis (LCC)
    Average retro-commissioning cost $0.27/sq. ft.; ~15% energy savings; simple payback ~0.7 years*
  Research available incentives
    Database of State Incentives for Renewables & Efficiency: http://www.dsireusa.org
*Based on Mills, et al. 2004 study (DOE Lawrence Berkeley National Laboratory)

## Slide 39: Steps to Take: Monitor Results
Continuously Monitor Results
  Develop an effective operation and management plan
  Be persistent!
  Iowa Public Building Benchmarking System

## Slide 40: Steps to Take: Monitor Results

## Slide 41
Questions?
Xiaohui “Joe” Zhou, PhD, PE
xhzhou@iastate.edu
Iowaenergycenter.org